## Fields Explanation
Equipment - NominalTonnage | User Input/Equipment Information | Y | Y
Equipment - Manufacturer | User Input/Equipment Information | N
Equipment - CompressorType | User Input/Equipment Information | Y | Y
Equipment - CondenserPhase | User Input/Equipment Information | Y | Y
Equipment - NumberofRefrigerantCircuits | User Input/Equipment Information | Y | Y
Equipment - Split or Packaged | User Input/Equipment Information | Y | Y
Equipment - RefrigerantType | User Input/Equipment Information | Y | Y
Equipment - CondenserModelNumber | User Input/Equipment Information | N
Equipment - MeteringDevice | User Input/Equipment Information | Y | Y
Equipment - AC or Heat Pump | User Input/Equipment Information | Y | Y
Equipment - BlowerMotorType | User Input/Equipment Information | Y | Y
Equipment - CondenserSerialNumber | User Input/Equipment Information | N
Equipment - LineSetLength | User Input/Equipment Information | Y | with 6
TRM_Building | User Input/Equipment Information | Y
Equipment - HeatSource | User Input/Equipment Information | N
CondenserConditionPre | User Input/State of Equipment | Y
EvaporatorConditionPre | User Input/State of Equipment | Y
BlowerConditionPre | User Input/State of Equipment | Y
FilterConditionPre | User Input/State of Equipment | Y
CondenserCleaned | User Input/State of Equipment | Y
EvaporatorCleaned | User Input/State of Equipment | Y
BlowerCleaned | User Input/State of Equipment | Y
FilterCleanedOrReplaced | User Input/State of Equipment | Y
EvaporatorNoCleanReason | User Input/State of Equipment | N(Y IF NOT CLEANED)
BlowerNoCleanReason | User Input/State of Equipment | N(Y IF NOT CLEANED)
AdjustBlowerSpeed | User Input/State of Equipment | Y
RecommendReplaceUnit | User Input/ Tech's Opinion for State of Equipment(Not Always Correct) | Y
Auto Eng Rvw | Calculation/Diagnosis | N
EffLossFlags_Text | Calculation | N
Notes (Internal) | User Input | N
Notes to contractor (Engineering) | User Input/Diagnosis | N
TechnicianNotes | User Input/Diagnosis | N
TechNote_CondenserAmps-tonnage_mismatch | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_CapacityToNominalHigh | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_CapacityToNominalLow | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_EvapTemp<32 | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_EvapTemp>45 | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_LLT<ODA | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_LLT>125 | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_RAtemplow | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
TechNote_SAtemplow | User Input/Diagnosis/Explanation why not in normal range | (if FLAGGED, Y)
AirFlowMethodID | User Input/Measurement Information | Y
Grill1Length | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill1Width | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill2Length | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill2Width | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill3Length | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill3Width | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill4Length | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
Grill4Width | User Input/Measurement Information | (If AirflowMethodID === 1, Y)
TI_AverageAirSpeed1 | User Input/Measurement Information | Depends on Grill chosen
TO_AverageAirSpeed1 | User Input/Measurement Information | Depends on Grill chosen
TI_AverageAirSpeed2 | User Input/Measurement Information | Depends on Grill chosen
TO_AverageAirSpeed2 | User Input/Measurement Information | Depends on Grill chosen
TI_AverageAirSpeed3 | User Input/Measurement Information | Depends on Grill chosen
TO_AverageAirSpeed3 | User Input/Measurement Information | Depends on Grill chosen
TI_AverageAirSpeed4 | User Input/Measurement Information | Depends on Grill chosen
TO_AverageAirSpeed4 | User Input/Measurement Information | Depends on Grill chosen
TI_ReturnAirStaticPressure | User Input/Measurement Information | (If AirflowMethodID === 2, Y)
TO_ReturnAirStaticPressure | User Input/Measurement Information | Y | (If AirflowMethodID === 2, Y)
TI_SupplyAirStaticPressure | User Input/Measurement Information | (If AirflowMethodID === 2, Y)
TO_SupplyAirStaticPressure | User Input/Measurement Information | Y | (If AirflowMethodID === 2, Y)
TI_TESP | Calculation : Sum of 59 + 61 | Y | (If AirflowMethodID === 2, Y)
TO_TESP | Calculation : Sum of 60 + 62 | Y | (If AirflowMethodID === 2, Y)
TI_SpeedSetting | User Input | Y | If Equipment-Fan Motor === "PSC"
TO_SpeedSetting | User Input | Y | If Equipment-Fan Motor === "PSC"
TI_iM_StaticPressureCFM | User Input if 42 == 3/Static Pressure if 42 == 2 | Y | (If AirflowMethodID === 2, Y)
TO_iM_StaticPressureCFM | User Input if 42 == 3/Static Pressure if 42 == 2 | Y | (If AirflowMethodID === 2, Y)
TI_CalculatedCFM | User Input if 42 == 3/Calculation based on iManifold's algorithm for Vane Anemometer if 42 == 1/Static Pressure if 42 == 2 | Y
TO_CalculatedCFM | User Input if 42 == 3/Calculation based on iManifold's algorithm for Vane Anemometer if 42 == 1/Static Pressure if 42 == 2 | Y
TI_CalculatedCFMPerTon | Calculation : 69/1 | Y
TO_CalculatedCFMPerTon | Calculation : 70/1 | Y
iManifold - TI CFM | Calculation based on iManifold's algorithm | Y
iManifold - TO CFM | Calculation based on iManifold's algorithm | Y
TO_CFMOutofRangeReason | User Input/Diagnosis/Explanation why not in normal range | IF(CFM Not in range +/-15%, Y)
TI_Rated_UF | User Input/Measurement Information | N
TO_Rated_UF | User Input/Measurement Information | N
TI_Tested_HZ | User Input/Measurement Information | N
TO_Tested_HZ | User Input/Measurement Information | N
TI_Tested_Volts | User Input/Measurement Information | N
TO_Tested_Volts | User Input/Measurement Information | N
TI_Tested_UF | User Input/Measurement Information | N
TO_Tested_UF | User Input/Measurement Information | N
TI_Tested_Amps | User Input/Measurement Information | N
TO_Tested_Amps | User Input/Measurement Information | N
RefrigerantAdjustment1 | User Input/Measurement Information/Adjustment made by technician to the system to fix it or make it better | N
AmountOz1 | User Input/Measurement Information/ Quantity for 86 | N
PercentChange1 | Calculation for 86 & 87 | N
Log - Refrigerant Adjustment1 | User Input/Notes | N
TI_SuctionPressure | User Input/iManfold Tool input/Measurement Information | Y
TO_SuctionPressure | User Input/iManfold Tool input/Measurement Information | Y
TI_DischargePressure | User Input/iManfold Tool input/Measurement Information | Y
TO_DischargePressure | User Input/iManfold Tool input/Measurement Information | Y
TI_EvaporatorTemperature | Calculation based on 90 | Y
TO_EvaporatorTemperature | Calculation based on 91 | Y
TI_CondenserTemperature | Calculation based on 92 | Y
TO_CondenserTemperature | Calculation based on 93 | Y
TI_Superheat | Calculation based on 90 & 107 | Y
TO_Superheat | Calculation based on 91 & 108 | Y
iManifold - Target superheat | Calculation based on 118 & 124 | Y
TechCalculatedTargetSH | User Input which overrides 100 | Y
TI_Subcooling | Calculation based on 96 & 109 | Y
TO_Subcooling | Calculation based on 97 & 110 | Y
TO_SubcoolingTarget | User Input | Y
iManifold - Target subcooling | Range based on 104 | Y
TechCalculatedTargetSC | User Input which overrides 105 | Y
TI_VaporLineTemperature | User Input/iManfold Tool input/Measurement Information | Y
TO_VaporLineTemperature | User Input/iManfold Tool input/Measurement Information | Y
TI_LiquidLineTemperature | User Input/iManfold Tool input/Measurement Information | Y
TO_LiquidLineTemperature | User Input/iManfold Tool input/Measurement Information | Y
TI_DischargeLineTemperature | User Input/iManfold Tool input/Measurement Information | Y
TO_DischargeLineTemperature | User Input/iManfold Tool input/Measurement Information | Y
SHSCOutOfRangeReason1 | User Input/Diagnosis/Explanation why not in normal range | N
TI_OutdoorAirTemp_WeatherService | Discard these fields/ Not needed, Already getting this data from Tool
TO_OutdoorAirTemp_WeatherService | Discard these fields/ Not needed, Already getting this data from Tool
TI_RelativeHumidity_WeatherService | Discard these fields/ Not needed, Already getting this data from Tool
TO_RelativeHumidity_WeatherService | Discard these fields/ Not needed, Already getting this data from Tool
TI_OutdoorAirDryBulbTemperature | User Input/iManfold Tool input/Measurement Information | Y
TO_OutdoorAirDryBulbTemperature | User Input/iManfold Tool input/Measurement Information | Y
TI_OutdoorAirWetBulbTemperature | Calculation based on 118 | Y
TO_OutdoorAirWetBulbTemperature | Calculation based on 119 | Y
TI_ReturnAirDryBulb | User Input/iManfold Tool input/Measurement Information | Y
TO_ReturnAirDryBulb | User Input/iManfold Tool input/Measurement Information | Y
TI_ReturnAirWetBulb | Calculation based on 122 | Y
TO_ReturnAirWetBulb | Calculation based on 123 | Y
TI_SupplyAirDryBulb | User Input/iManfold Tool input/Measurement Information | Y
TO_SupplyAirDryBulb | User Input/iManfold Tool input/Measurement Information | Y
TI_SupplyAirWetBulb | Calculation based on 126 | Y
TO_SupplyAirWetBulb | Calculation based on 127 | Y
TI_ReturnAirEnthalpy | Calculation based on 124 | Y
TO_ReturnAirEnthalpy | Calculation based on 125 | Y
TI_SupplyAirEnthalpy | Calculation based on 128 | Y
TO_SupplyAirEnthalpy | Calculation based on 129 | Y
TI_DeltahOrChangeInEnthalpy | Calculation : 130-132 | Y
TO_DeltahOrChangeInEnthalpy | Calculation : 131-133 | Y
TI_SensibleCapacity | Calculation | Y
TO_SensibleCapacity | Calculation | Y
TI_LatentCapacity | Calculation | Y
TO_LatentCapacity | Calculation | Y
TI_TotalUnadjustedCapacity | Calculation | Y
TO_TotalUnadjustedCapacity | Calculation | Y
TI_TotalCapacityCorrectedToARIConditions | Calculation | Y
TO_TotalCapacityCorrectedToARIConditions | Calculation | Y
TI_CapacityToNominal | Calculation | Y
TO_CapacityToNominal | Calculation | Y
TI_UnadjustedEER | Calculation | Y
TO_UnadjustedEER | Calculation | Y
TI_EERCorrectedToARIConditions | Calculation | Y
TO_EERCorrectedToARIConditions | Calculation | Y
EERpre | Calculation | Y
EERpost | Calculation | Y
DeemedEfficiencyLoss | Calculation | Y
TO_iManifoldWarning | Diagnosis for the codes | Y
EfficiencyLossEstimate | Calculation | Y

## Features
Equipment - NominalTonnage | Equipment - CompressorType | Equipment - CondenserPhase | Equipment - NumberofRefrigerantCircuits | Equipment - Split or Packaged | Equipment - RefrigerantType | Equipment - MeteringDevice | Equipment - AC or Heat Pump | Equipment - BlowerMotorType | Equipment - LineSetLength

## Rules for Fields
Rules | Range/Number/Low/High | Notes
TI_ReturnAirStaticPressure/TO_ReturnAirStaticPressure | 0.2-0.4 | Screenshot
TI_SupplyAirStaticPressure/TO_SupplyAirStaticPressure | 0.2-0.4 | Screenshot
TI_TESP/TO_TESP | > 0.75 | Low CFM
TI_TESP/TO_TESP | <0.30 | High CFM
TI_iM_StaticPressureCFM/TO_iM_StaticPressureCFM | <10% Nominal Airflow/Ton | Low Airflow
TI_iM_StaticPressureCFM/TO_iM_StaticPressureCFM | >10% Nominal Airflow/Ton | High Airflow
Low Airflow | High Delta-H | Inversely proportional
High Airflow | Low Delta-H | Inversely proportional
Explanation
Equipment - BlowerMotorType
PSC | 400/Ton
VFD/Three Phase/ECM/X13 | 350/Ton

## Mapping of Code to Diagnosis
Diagnosis | Overcharge | SEVERE OVERCHARGED/FAILED OPEN TXV | Undercharge | High Side Restriction | Low Side Restriction | Low Evap Air | airflow problem or air bypassing evaporator coil | Dirty Condensor | Low Ambient Air Temp | Bad Compressor Valves | TXV Bulb bad | Loose TXV Bulb | TXV Bulb Not Insulated | bad valves or internal bypass | Slight Undercharge
| 21212 | 22202 |  |  |  |  | 20011 | 21211 |  |  |  | 21101 | 21101 | 22011 | 21110
[8 empty] | 21222 |  |  |  | 22101 | 22101 | 22010
[8 empty] | 22212 |  |  |  | 22000 | 22000
[8 empty] | 22222 |  |  |  | 22001 | 22001
22211
| 12202/12201 |  | 10020 | 10022 |  |  | 12200 |  |  |  |  | 21101 | 21101 | 12010/12011/12012/12001